## Tunnel Fan Comparison
Tunnel Ventilation Fan Comparison Spreadsheet
| Adapted from 'Tunnel Fan Comparison Spreadsheet 2014', The University of Georgia - Michael Czarick (mczarick@uga.edu) | [7 empty] | Calculator to assist with the prediction of fan hours based on fan monitoring data collected in Australia
| Enter green values in all sections (don't enter "$" or "," ). Imperial to metric conversions on the attached worksheets | [7 empty] | Maximum length of typical batch |  |  | 56
[9 empty] | Number of batches per year |  |  | 5.5
| Input poultry house information | [7 empty] | Calculated number of production days per year |  |  | 308
| House Length (m) = |  | 150 | Electricity Rate ($ per kW·h) = |  |  | 0.15 |  | Minimum hours (on average) per fan per year |  |  | 1760
| House Width (m) = |  | 15.3 | Estimated Yearly Operating Hours per fan = |  |  | 2000 |  | Maximum hours (on average) per fan per year |  |  | 2400
| Side Wall Height (m) = |  | 2.6 | Minimum Design Air Velocity (m/s) = |  |  | 3
| Ceiling Peak Height (m) = |  | 2.6 | Minimum recommended fan capacity m³/hr (air exchange) = |  |  | 461699.5447 |  | Calculated fan capacity based on in-shed 'Minimum Design Air Velocity
| Open/Dropped Ceiling (o/d) (m) = |  | o | Change minimum fan capacity ("0" if you don't wish to modify) |  |  | 429624 |  |  | 429624
Input — tunnel fan information Obtain the most recent data for the fans you are considering from independent test report (available from your fan supplier). Note: air flow data and fan prices listed below were obtained prior to April 2012
Tunnel Fan Model | Air Flow (m³/hour) |  |  |  | Energy Efficiency | Price of Fan | Data Source
| 12.5 | 25 | 37.5 | 50 | m³/h per watt @ 25 Pa | ($, excl. GST)
INSERT FAN NAME AND DATA HERE
INSERT FAN NAME AND DATA HERE
INSERT FAN NAME AND DATA HERE
INSERT FAN NAME AND DATA HERE
INSERT FAN NAME AND DATA HERE
Hired Hand 6603-7403 52" (60Hz) CONE 1hp | 46553 | 43665 | 40946 | 37548 | 35 | 1133 | BESS test 02466
Hired Hand 6603-6527 52.5" - Butterfly damper (60Hz) CONE 1hp | 46720 | 43665 | 39925 | 35850 | 32.8 | 1198.32 | BESS test 05334
Hired Hand 6603-3000 52.5" - CONE 1.5hp | 43665 | 40605 | 37038 | 32790 | 32.96 | 1542.09 | BESS test 07090
Hired Hand 6603-8010 54" - CONE 1.5hp | 45363 | 42645 | 39417 | 35509 | 41.14 | 1464 | BESS test 08257a
Munters Euroemme EM50 - 1hp | 32978 | 30786 | 27713 | 24365 | 26.5 | 908 | BESS test 02333
Munters Euroemme EM50 - 1.5hp | 40042 | 38272 | 36028 | 33717 | 21.76 | 931.25 | BESS test 02332
Munters Euroemme EC-50 (60Hz, 1 phase) CONE 1hp | 38590 | 35870 | 32640 | 28560 | 33.66 | 1101 | BESS test 02335
Munters Euroemme EC-50 CONE 1.5hp | 44401.413 | 42526.1004 | 40450.726 | 38017.6614 | 26.7323 | 1121 | BESS test 02334
Munters WF541V3CD-50 – Butterfly damper, 54" (1hp, CONE) | 44300 | 40800 | 36900 | 32600 | 36.5 | 1550 | BESS test 11353
Munters WF501V3CD-50 – Butterfly damper, 50" (1hp, CONE) | 40800 | 36800 | 30300 | 26300 | 31.9 | 1500 | BESS test 11351
Munters WF5015V3CD-50 – Butterfly damper, 50" (1.5hp, CONE) | 44600 | 41500 | 37900 | 34200 | 30.1 | 1500 | Best test 11352
American Coolair MNBF60M (60Hz) 1.5 hp | 49470 | 46070 | 41310 | 34340 | 31.2 | 2189 | BESS test 09248
American Coolair MNBFC60M (60Hz) CONE 1.5 hp | 54400 | 50320 | 44880 | 36890 | 33.8 | 2445 | BESS test 09257
American Coolair MNBFA54L (60Hz) 1hp | 40235.6 | 37655 | 34690.2 | 29998.2 | 32.64 | 1758 | American Coolair brochure Jan 2010 (ANSI/AMCA Standard 210-07)
American Coolair MNBFA54M (60Hz) 1.5hp) | 45042 | 42720 | 40294 | 37303 | 26.33 | 1830 | American Coolair brochure Jan 2010 (ANSI/AMCA Standard 210-07)
American Coolair MNBFA54N (60Hz) 2hp | 48875 | 46711 | 44529 | 42089.6 | 20.1 | 1892 | American Coolair brochure Jan 2010 (ANSI/AMCA Standard 210-07)
American Coolair MNBFA48L (60Hz) 1hp with CONE | 31387 | 29053 | 26651 | 23774 | 31.3 | 1458 | American Coolair brochure Jan 2010 (ANSI/AMCA Standard 210-07)
American Coolair MNCFC52L (60Hz) CONE 1hp | 41310 | 37570 | 33150 | 26350 | 30.43 | 1708 | American Coolair brochure Oct 2007 (ANSI/AMCA Standard 210-99)
American Coolair MNBCCE54L (60 Hz) CONE 1hp | 43494 | 40266 | 36019 | 30752 | 46.2 | 1888 | BESS test 10240
American Coolair MNCFE52L (60Hz) 1hp | 35530 | 32300 | 28050 | 21590 | 33.49 | 1470 | BESS test 99160
Chore-Time 52157-51 (54", 1.5hp, 3 blade) CONE | 51310 | 47912 | 43834 | 39926 | 33.8 | 1542 | BESS test 09084
Multifan MF130 0.75kW (50.5", 1.0hp, 3 blade) | 35400 | 32100 | 27200 | 22500 | 27.3 | 720 | BESS test 12123
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) | 40200 | 37800 | 34600 | 30600 | 25.4 | 720 | BESS test 12126
Multifan MF130 0.75 kW (50.5", 1.0 hp, 3 blade) CONE | 38800 | 35800 | 32400 | 28200 | 30.6 | 890 | BESS test 12136
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) CONE | 44100 | 41700 | 38900 | 36100 | 28.5 | 890 | BESS test 12138 |  |  |  |  | Energy Efficiency and Air Flow Ratio ratings
[11 empty] | Rating | Air Flow Ratio | Energy Efficiency
[12 empty] | Air flow (50Pa) / | (@ 25 Pa)
air flow (12 Pa)
[11 empty] | poor | Less than 0.70 | Less than 32.3
!
[11 empty] | min. acceptable | 0.70 - 0.72 | 32.3 - 33.8
*
[11 empty] | good | 0.73 - 0.77 | 34.0 - 35.5
* *
[11 empty] | excellent | 0.78 - 0.82 | 35.7 - 37.2
* * *
[11 empty] | outstanding | 0.83 + | 37.4 +
* * * *
Output — Per Shed Check that fan numbers and air velocity meet your requirements, then see how the fans compare ! | [9 empty] | RATINGS |  |  |  | EVAPORATIVE COOLING PAD REQUIREMENTS |  |  | TOTAL FAN RUNNING COSTS PER SHED |  |  |  |  | RANKINGS – all fans
Model # | Design static | Tunnel Fan | Number of fans | Change number | Total air moving capacity | Power Consumption | Total fan operating | Air velocity | Est. Wind-chill @ 29.4°C | Air Flow Ratio | Air Flow Ratio | Energy Efficiency | Energy Efficiency | Total Pad Area | Pad water usage | Pad water usage |  | Five Year |  | Ten Year |  | Energy Effic. | Airflow | 10 Yr Cost | Energy Eff. | Pressure | m³/hr for velocity | velocity check | Airflow for Evap
| pressure | capacity | required * | of fans? (no=0) | at design static pressure | All fans @ 25 Pa | cost (yearly) | (all fans operating) | (all fans operating) |  |  | (m³/h/watt @ 25Pa) | (m³/h/watt @ 25Pa) | (minimum for 150mm thick pad) | (32.2°C - 50% Rh) | (37.8°C - 20 % Rh) | Purchase cost | Electricity | Total | Electricity | Total | @ 25 Pa | Ratio |  | Rating | Rating |  |  | cooling Calcs
INSERT FAN NAME AND DATA HERE | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 429624 | 429624 | 0
INSERT FAN NAME AND DATA HERE | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 429624 | 429624 | 0
INSERT FAN NAME AND DATA HERE | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 429624 | 429624 | 0
INSERT FAN NAME AND DATA HERE | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 429624 | 429624 | 0
INSERT FAN NAME AND DATA HERE | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 429624 | 429624 | 0
Hired Hand 6603-7403 52" (60Hz) CONE 1hp | 37.5 | 40946 | 11 | 0 | 450400 | 13.7 | 4120 | 3.15 | 8.8533 | 0.81 | EXCELLENT | 35 | GOOD | 74.6694 | 1504.336 | 2842.024 | 12463 | 20600 | 33063 | 41200 | 53663 | 4 | 6 | 2 | 2 | 3 | 429624 | 429624 | 46553
Hired Hand 6603-6527 52.5" - Butterfly damper (60Hz) CONE 1hp | 37.5 | 39925 | 11 | 0 | 439200 | 14.6 | 4390 | 3.07 | 8.4153 | 0.77 | GOOD | 32.8 | MIN ACCEPTABLE | 74.9373 | 1466.928 | 2771.352 | 13181.52 | 21950 | 35131.52 | 43900 | 57081.52 | 10 | 9 | 4 | 1 | 2 | 429624 | 429624 | 46720
Hired Hand 6603-3000 52.5" - CONE 1.5hp | 37.5 | 37038 | 12 | 0 | 444500 | 14.8 | 4440 | 3.1 | 8.5782 | 0.75 | GOOD | 32.96 | MIN ACCEPTABLE | 76.4042 | 1484.63 | 2804.795 | 18505.08 | 22200 | 40705.08 | 44400 | 62905.08 | 9 | 13 | 9 | 1 | 2 | 429624 | 429624 | 43665
Hired Hand 6603-8010 54" - CONE 1.5hp | 37.5 | 39417 | 11 | 0 | 433600 | 11.4 | 3420 | 3.03 | 8.2004 | 0.78 | EXCELLENT | 41.14 | OUTSTANDING | 72.7607 | 1448.224 | 2736.016 | 16104 | 17100 | 33204 | 34200 | 50304 | 2 | 7 | 1 | 4 | 3 | 429624 | 429624 | 45363
Munters Euroemme EM50 - 1hp | 37.5 | 27713 | 16 | 0 | 443400 | 18.6 | 5580 | 3.1 | 8.5782 | 0.74 | GOOD | 26.5 | POOR | 76.939 | 1480.956 | 2797.854 | 14528 | 27900 | 42428 | 55800 | 70328 | 21 | 15 | 18 | 0 | 2 | 429624 | 429624 | 32978
Munters Euroemme EM50 - 1.5hp | 37.5 | 36028 | 12 | 0 | 432300 | 21.1 | 6330 | 3.02 | 8.1471 | 0.84 | OUTSTANDING | 21.76 | POOR | 70.0647 | 1443.882 | 2727.813 | 11175 | 31650 | 42825 | 63300 | 74475 | 24 | 3 | 24 | 0 | 4 | 429624 | 429624 | 40042
Munters Euroemme EC-50 (60Hz, 1 phase) CONE 1hp | 37.5 | 32640 | 14 | 0 | 457000 | 14.9 | 4480 | 3.19 | 9.0764 | 0.74 | GOOD | 33.66 | MIN ACCEPTABLE | 78.7781 | 1526.38 | 2883.67 | 15414 | 22400 | 37814 | 44800 | 60214 | 7 | 15 | 7 | 1 | 2 | 429624 | 429624 | 38590
Munters Euroemme EC-50 CONE 1.5hp | 37.5 | 40450.726 | 11 | 0 | 445000 | 17.5 | 5250 | 3.11 | 8.6329 | 0.86 | OUTSTANDING | 26.7323 | POOR | 71.2184 | 1486.3 | 2807.95 | 12331 | 26250 | 38581 | 52500 | 64831 | 20 | 1 | 11 | 0 | 4 | 429624 | 429624 | 44401.413
Munters WF541V3CD-50 – Butterfly damper, 54" (1hp, CONE) | 37.5 | 36900 | 12 | 0 | 442800 | 13.4 | 4020 | 3.09 | 8.5237 | 0.74 | GOOD | 36.5 | EXCELLENT | 77.5153 | 1478.952 | 2794.068 | 18600 | 20100 | 38700 | 40200 | 58800 | 3 | 15 | 6 | 3 | 2 | 429624 | 429624 | 44300
Munters WF501V3CD-50 – Butterfly damper, 50" (1hp, CONE) | 37.5 | 30300 | 15 | 0 | 454500 | 17.3 | 5190 | 3.17 | 8.9645 | 0.64 | POOR | 31.9 | POOR | 89.2388 | 1518.03 | 2867.895 | 22500 | 25950 | 48450 | 51900 | 74400 | 12 | 22 | 23 | 0 | 0 | 429624 | 429624 | 40800
Munters WF5015V3CD-50 – Butterfly damper, 50" (1.5hp, CONE) | 37.5 | 37900 | 12 | 0 | 454800 | 16.5 | 4960 | 3.18 | 9.0204 | 0.77 | GOOD | 30.1 | POOR | 78.0402 | 1519.032 | 2869.788 | 18000 | 24800 | 42800 | 49600 | 67600 | 17 | 9 | 13 | 0 | 2 | 429624 | 429624 | 44600
American Coolair MNBF60M (60Hz) 1.5 hp | 37.5 | 41310 | 11 | 0 | 454400 | 16.2 | 4870 | 3.17 | 8.9645 | 0.69 | POOR | 31.2 | POOR | 79.3482 | 1517.696 | 2867.264 | 24079 | 24350 | 48429 | 48700 | 72779 | 14 | 20 | 21 | 0 | 0 | 429624 | 429624 | 49470
American Coolair MNBFC60M (60Hz) CONE 1.5 hp | 37.5 | 44880 | 10 | 0 | 448800 | 14.9 | 4470 | 3.13 | 8.7427 | 0.68 | POOR | 33.8 | MIN ACCEPTABLE | 79.3234 | 1498.992 | 2831.928 | 24450 | 22350 | 46800 | 44700 | 69150 | 5 | 21 | 16 | 1 | 0 | 429624 | 429624 | 54400
American Coolair MNBFA54L (60Hz) 1hp | 37.5 | 34690.2 | 13 | 0 | 451000 | 15 | 4500 | 3.15 | 8.8533 | 0.75 | GOOD | 32.64 | MIN ACCEPTABLE | 76.2705 | 1506.34 | 2845.81 | 22854 | 22500 | 45354 | 45000 | 67854 | 11 | 13 | 14 | 1 | 2 | 429624 | 429624 | 40235.6
American Coolair MNBFA54M (60Hz) 1.5hp) | 37.5 | 40294 | 11 | 0 | 443200 | 17.8 | 5350 | 3.09 | 8.5237 | 0.83 | OUTSTANDING | 26.33 | POOR | 72.2458 | 1480.288 | 2796.592 | 20130 | 26750 | 46880 | 53500 | 73630 | 22 | 4 | 22 | 0 | 4 | 429624 | 429624 | 45042
American Coolair MNBFA54N (60Hz) 2hp | 37.5 | 44529 | 10 | 0 | 445300 | 23.2 | 6970 | 3.11 | 8.6329 | 0.86 | OUTSTANDING | 20.1 | POOR | 71.2671 | 1487.302 | 2809.843 | 18920 | 34850 | 53770 | 69700 | 88620 | 25 | 1 | 25 | 0 | 4 | 429624 | 429624 | 48875
American Coolair MNBFA48L (60Hz) 1hp with CONE | 37.5 | 26651 | 17 | 0 | 453100 | 15.8 | 4730 | 3.16 | 8.9088 | 0.76 | GOOD | 31.3 | POOR | 77.8039 | 1513.354 | 2859.061 | 24786 | 23650 | 48436 | 47300 | 72086 | 13 | 11 | 20 | 0 | 2 | 429624 | 429624 | 31387
American Coolair MNCFC52L (60Hz) CONE 1hp | 37.5 | 33150 | 13 | 0 | 431000 | 16.1 | 4820 | 3.01 | 8.094 | 0.64 | POOR | 30.43 | POOR | 78.3071 | 1439.54 | 2719.61 | 22204 | 24100 | 46304 | 48200 | 70404 | 16 | 22 | 19 | 0 | 0 | 429624 | 429624 | 41310
American Coolair MNBCCE54L (60 Hz) CONE 1hp | 37.5 | 36019 | 12 | 0 | 432200 | 10.5 | 3140 | 3.02 | 8.1471 | 0.71 | MIN ACCEPTABLE | 46.2 | OUTSTANDING | 76.105 | 1443.548 | 2727.182 | 22656 | 15700 | 38356 | 31400 | 54056 | 1 | 19 | 3 | 4 | 1 | 429624 | 429624 | 43494
American Coolair MNCFE52L (60Hz) 1hp | 37.5 | 28050 | 16 | 0 | 448800 | 15.4 | 4630 | 3.13 | 8.7427 | 0.61 | POOR | 33.49 | MIN ACCEPTABLE | 82.893 | 1498.992 | 2831.928 | 23520 | 23150 | 46670 | 46300 | 69820 | 8 | 25 | 17 | 1 | 0 | 429624 | 429624 | 35530
Chore-Time 52157-51 (54", 1.5hp, 3 blade) CONE | 37.5 | 43834 | 10 | 0 | 438300 | 14.2 | 4250 | 3.06 | 8.3613 | 0.78 | EXCELLENT | 33.8 | MIN ACCEPTABLE | 74.8177 | 1463.922 | 2765.673 | 15420 | 21250 | 36670 | 42500 | 57920 | 5 | 7 | 5 | 1 | 3 | 429624 | 429624 | 51310
Multifan MF130 0.75kW (50.5", 1.0hp, 3 blade) | 37.5 | 27200 | 16 | 0 | 435200 | 18.8 | 5640 | 3.04 | 8.2539 | 0.64 | POOR | 27.3 | POOR | 82.5897 | 1453.568 | 2746.112 | 11520 | 28200 | 39720 | 56400 | 67920 | 19 | 22 | 15 | 0 | 0 | 429624 | 429624 | 35400
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) | 37.5 | 34600 | 13 | 0 | 449800 | 19.3 | 5800 | 3.14 | 8.7979 | 0.76 | GOOD | 25.4 | POOR | 76.203 | 1502.332 | 2838.238 | 9360 | 29000 | 38360 | 58000 | 67360 | 23 | 11 | 12 | 0 | 2 | 429624 | 429624 | 40200
Multifan MF130 0.75 kW (50.5", 1.0 hp, 3 blade) CONE | 37.5 | 32400 | 14 | 0 | 453600 | 16.4 | 4910 | 3.17 | 8.9645 | 0.73 | GOOD | 30.6 | POOR | 79.2068 | 1515.024 | 2862.216 | 12460 | 24550 | 37010 | 49100 | 61560 | 15 | 18 | 8 | 0 | 2 | 429624 | 429624 | 38800
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) CONE | 37.5 | 38900 | 12 | 0 | 466800 | 17.6 | 5270 | 3.26 | 9.4737 | 0.82 | EXCELLENT | 28.5 | POOR | 77.1654 | 1559.112 | 2945.508 | 10680 | 26350 | 37030 | 52700 | 63380 | 18 | 5 | 10 | 0 | 3 | 429624 | 429624 | 44100
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
|  |  |  | 0 | [22 empty] | 429624 | 429624 | 0
Note on H7: Note: you may be billed for electricity based on peak power draw plus total power usage, which is different from this method of calculating 'average' fan costs. Also, Some farms may be billed for kVa rather than kW.
Note on H8: Use the calculator in the purple cells to the right to estimate fan operating hours for your sheds based on what has been measured at Broiler sheds in Qld, NSW and Vic.
Note on D10: Note: if you have ceiling baffles, set the 'Ceiling Peak Height' to the height of the baffle above the shed floor.
Note on D11: Note: Dropped ceilings are used in the United States but rarely seen in Australia.
Note on H11: If you wish to calculate the number of fans required to achieve the 'Minimum Design Air Velocity', use the value in the orange box to the right, otherwise use '0' (zero)
Note on K64: Refer to the above table for ratings
Note on B66: This is the pressure at the fans, so will usually be greater than the shed static pressure
Note on G66: Note: if calculating peak power load, you may need to use the power consumption at higher static pressure - refer to your fan test report
Note on O67: Based on Poultry Housing Tips—Pad System Cooling, Installation and Management. (July 2001, vol. 13 No.8 — 1m² per 6858 m³/hr
Note on P67: Based on Poultry Housing Tips—Six-inch pad system water usage and pipe sizing. (June 2006, vol. 18 No.6

## Imperial to metric Conv.
To convert Imperial/English units into metric, type the Imperial/English value into the yellow cell and read the metric value from the cell with blue text
Flow rate |  |  | Speed |  | Distance |  | Energy Efficiency |  | Pressure |  | Temperature
CFM | m³/h | m³/s | feet/min | m/s | ft | m | CFM per watt | m³/h per watt | inch H2O | Pa | °F | °C
1 | 2 | 0.001 | 1 | 0.01 | 1 | 0.3048 | 1 | 1.699 | 1 | 249 | 1 | -17.2222
2000 | 3398.0418 | 0.9439 | 50 | 0.254 | 10 | 3.048 | 10 | 16.9902 | 0.01 | 2.49 | 32 | 0
2500 | 4247.5522 | 1.1799 | 100 | 0.508 | 15 | 4.572 | 11 | 18.6892 | 0.02 | 4.98 | 34 | 1.1111
3000 | 5097.0627 | 1.4159 | 150 | 0.762 | 20 | 6.096 | 12 | 20.3883 | 0.03 | 7.47 | 36 | 2.2222
3500 | 5946.5731 | 1.6518 | 200 | 1.016 | 25 | 7.62 | 13 | 22.0873 | 0.04 | 9.96 | 38 | 3.3333
4000 | 6796.0835 | 1.8878 | 250 | 1.27 | 30 | 9.144 | 14 | 23.7863 | 0.05 | 12.45 | 40 | 4.4444
4500 | 7645.594 | 2.1238 | 300 | 1.524 | 35 | 10.668 | 15 | 25.4853 | 0.06 | 14.94 | 42 | 5.5556
5000 | 8495.1044 | 2.3598 | 350 | 1.778 | 40 | 12.192 | 16 | 27.1843 | 0.07 | 17.43 | 44 | 6.6667
5500 | 9344.6149 | 2.5957 | 400 | 2.032 | 45 | 13.716 | 17 | 28.8834 | 0.08 | 19.92 | 46 | 7.7778
6000 | 10194.1253 | 2.8317 | 450 | 2.286 | 50 | 15.24 | 18 | 30.5824 | 0.09 | 22.41 | 48 | 8.8889
6500 | 11043.6358 | 3.0677 | 500 | 2.54 | 55 | 16.764 | 19 | 32.2814 | 0.1 | 24.9 | 50 | 10
7000 | 11893.1462 | 3.3037 | 550 | 2.794 | 60 | 18.288 | 20 | 33.9804 | 0.11 | 27.39 | 52 | 11.1111
7500 | 12742.6566 | 3.5396 | 600 | 3.048 | 65 | 19.812 | 21 | 35.6794 | 0.12 | 29.88 | 54 | 12.2222
8000 | 13592.1671 | 3.7756 | 650 | 3.302 | 100 | 30.4801 | 22 | 37.3785 | 0.13 | 32.37 | 56 | 13.3333
8500 | 14441.6775 | 4.0116 | 700 | 3.556 | 300 | 91.4402 | 23 | 39.0775 | 0.14 | 34.86 | 58 | 14.4444
9000 | 15291.188 | 4.2476 | 750 | 3.81 | 350 | 106.6802 | 24 | 40.7765 | 0.15 | 37.35 | 60 | 15.5556
9500 | 16140.6984 | 4.4835 | 800 | 4.064 | 400 | 121.9202 | 25 | 42.4755 | 0.16 | 39.84 | 62 | 16.6667
10000 | 16990.2089 | 4.7195 | 850 | 4.318 | 450 | 137.1603 | 26 | 44.1745 | 0.17 | 42.33 | 64 | 17.7778
10500 | 17839.7193 | 4.9555 | 900 | 4.572 | 500 | 152.4003 | 27 | 45.8736 | 0.18 | 44.82 | 66 | 18.8889
11000 | 18689.2297 | 5.1915 |  |  | 550 | 167.6403 | 28 | 47.5726 | 0.19 | 47.31 | 68 | 20
11500 | 19538.7402 | 5.4274 |  |  | 600 | 182.8804 | 29 | 49.2716 | 0.2 | 49.8 | 70 | 21.1111
12000 | 20388.2506 | 5.6634 |  |  | 650 | 198.1204 | 30 | 50.9706 | 0.21 | 52.29 | 72 | 22.2222
12500 | 21237.7611 | 5.8994 |  |  | 700 | 213.3604 |  |  | 0.22 | 54.78 | 74 | 23.3333
13000 | 22087.2715 | 6.1354 |  |  | 750 | 228.6005 | Energy Efficiency |  | 0.23 | 57.27 | 76 | 24.4444
13500 | 22936.782 | 6.3713 |  |  |  |  | Watts per CFM | Watts per m³/h | 0.24 | 59.76 | 78 | 25.5556
14000 | 23786.2924 | 6.6073 |  |  |  |  | 1 | 0.58857 | 0.25 | 62.25 | 80 | 26.6667
14500 | 24635.8028 | 6.8433 |  |  |  |  | 0.1 | 0.058857 | 0.26 | 64.74 | 82 | 27.7778
15000 | 25485.3133 | 7.0793 |  |  |  |  | 0.090909 | 0.053507 | 0.27 | 67.23 | 84 | 28.8889
15500 | 26334.8237 | 7.3152 |  |  |  |  | 0.083333 | 0.049048 | 0.28 | 69.72 | 86 | 30
16000 | 27184.3342 | 7.5512 |  |  |  |  | 0.076923 | 0.045275 | 0.29 | 72.21 | 88 | 31.1111
16500 | 28033.8446 | 7.7872 |  |  |  |  | 0.071429 | 0.042041 | 0.3 | 74.7 | 90 | 32.2222
17000 | 28883.3551 | 8.0232 |  |  |  |  | 0.066667 | 0.039238 |  |  | 92 | 33.3333
17500 | 29732.8655 | 8.2591 |  |  |  |  | 0.0625 | 0.036786 |  |  | 94 | 34.4444
18000 | 30582.3759 | 8.4951 |  |  |  |  | 0.058824 | 0.034622 |  |  | 96 | 35.5556
18500 | 31431.8864 | 8.7311 |  |  |  |  | 0.055556 | 0.032699 |  |  | 98 | 36.6667
19000 | 32281.3968 | 8.9671 |  |  |  |  | 0.052632 | 0.030978 |  |  | 100 | 37.7778
19500 | 33130.9073 | 9.203 |  |  |  |  | 0.05 | 0.029429 |  |  | 102 | 38.8889
20000 | 33980.4177 | 9.439 |  |  |  |  | 0.047619 | 0.028027 |  |  | 104 | 40
20500 | 34829.9282 | 9.675 |  |  |  |  | 0.045455 | 0.026753 |  |  | 106 | 41.1111
21000 | 35679.4386 | 9.911 |  |  |  |  | 0.043478 | 0.02559 |  |  | 108 | 42.2222
[7 empty] | 0.041667 | 0.024524
50000 | 84951.0443 | 23.5975 |  |  |  |  | 0.04 | 0.023543
100000 | 169902.0886 | 47.195 |  |  |  |  | 0.038462 | 0.022637
150000 | 254853.1329 | 70.7925 |  |  |  |  | 0.037037 | 0.021799
200000 | 339804.1772 | 94.39 |  |  |  |  | 0.035714 | 0.021021
250000 | 424755.2215 | 117.9876 |  |  |  |  | 0.034483 | 0.020296
300000 | 509706.2658 | 141.5851 |  |  |  |  | 0.033333 | 0.019619

## Metric to Imperial Conv.
To convert metric units into Imperial/English, type the metric value into the yellow cell and read the Imperial/English value from the cell with blue text
Flow Rate |  | Speed |  | Distance |  | Energy Efficiency |  | Energy Efficiency |  | Pressure |  | Temperature
m³/h | CFM | m/s | feet/min | m | ft | m³/h per watt | CFM per watt | Watts per m³/h | Watts per CFM | Pa | inch H2O | °C | °F
20 | 11.7715 | 1 | 196.85 | 1 | 3.2808 | 1 | 0.58857 | 1 | 1.699 | 1 | 0.0040161 | 1 | 33.8
1000 | 588.5743 | 0.25 | 49.2125 | 5 | 16.4042 | 10 | 5.8857 | 0.1 | 0.1699 | 2 | 0.0080321 | 0 | 32
5000 | 2942.8714 | 0.5 | 98.425 | 6 | 19.685 | 11 | 6.4743 | 0.090909 | 0.15446 | 4 | 0.016064 | 1 | 33.8
10000 | 5885.7428 | 0.75 | 147.6375 | 7 | 22.9658 | 12 | 7.0629 | 0.083333 | 0.14159 | 6 | 0.024096 | 2 | 35.6
11000 | 6474.3171 | 1 | 196.85 | 8 | 26.2466 | 13 | 7.6515 | 0.076923 | 0.13069 | 8 | 0.032129 | 3 | 37.4
12000 | 7062.8914 | 1.25 | 246.0625 | 9 | 29.5275 | 14 | 8.24 | 0.071429 | 0.12136 | 10 | 0.040161 | 4 | 39.2
13000 | 7651.4657 | 1.5 | 295.275 | 10 | 32.8083 | 15 | 8.8286 | 0.066667 | 0.11327 | 12 | 0.048193 | 5 | 41
14000 | 8240.04 | 1.75 | 344.4875 | 11 | 36.0891 | 16 | 9.4172 | 0.0625 | 0.10619 | 14 | 0.056225 | 6 | 42.8
15000 | 8828.6142 | 2 | 393.7 | 12 | 39.37 | 17 | 10.0058 | 0.058824 | 0.099942 | 16 | 0.064257 | 7 | 44.6
16000 | 9417.1885 | 2.25 | 442.9125 | 13 | 42.6508 | 18 | 10.5943 | 0.055556 | 0.09439 | 18 | 0.072289 | 8 | 46.4
17000 | 10005.7628 | 2.5 | 492.125 | 14 | 45.9316 | 19 | 11.1829 | 0.052632 | 0.089422 | 20 | 0.080321 | 9 | 48.2
18000 | 10594.3371 | 2.75 | 541.3375 | 15 | 49.2124 | 20 | 11.7715 | 0.05 | 0.084951 | 22 | 0.088353 | 10 | 50
19000 | 11182.9114 | 3 | 590.55 | 16 | 52.4933 | 21 | 12.3601 | 0.047619 | 0.080906 | 24 | 0.096386 | 11 | 51.8
20000 | 11771.4857 | 3.25 | 639.7625 | 17 | 55.7741 | 22 | 12.9486 | 0.045455 | 0.077228 | 26 | 0.10442 | 12 | 53.6
21000 | 12360.0599 | 3.5 | 688.975 | 18 | 59.0549 | 23 | 13.5372 | 0.043478 | 0.07387 | 28 | 0.11245 | 13 | 55.4
22000 | 12948.6342 | 3.75 | 738.1875 | 19 | 62.3358 | 24 | 14.1258 | 0.041667 | 0.070793 | 30 | 0.12048 | 14 | 57.2
23000 | 13537.2085 | 4 | 787.4 | 20 | 65.6166 | 25 | 14.7144 | 0.04 | 0.067961 | 32 | 0.12851 | 15 | 59
24000 | 14125.7828 | 4.25 | 836.6125 |  |  | 26 | 15.3029 | 0.038462 | 0.065347 | 34 | 0.13655 | 16 | 60.8
25000 | 14714.3571 | 4.5 | 885.825 | 100 | 328.083 | 27 | 15.8915 | 0.037037 | 0.062927 | 36 | 0.14458 | 17 | 62.6
26000 | 15302.9314 | 4.75 | 935.0375 | 110 | 360.8913 | 28 | 16.4801 | 0.035714 | 0.060679 | 38 | 0.15261 | 18 | 64.4
27000 | 15891.5056 |  |  | 120 | 393.6996 | 29 | 17.0687 | 0.034483 | 0.058587 | 40 | 0.16064 | 19 | 66.2
28000 | 16480.0799 |  |  | 130 | 426.5079 | 30 | 17.6572 | 0.033333 | 0.056634 | 42 | 0.16867 | 20 | 68
29000 | 17068.6542 |  |  | 140 | 459.3162 | 31 | 18.2458 | 0.032258 | 0.054807 | 44 | 0.17671 | 21 | 69.8
30000 | 17657.2285 |  |  | 150 | 492.1245 | 32 | 18.8344 | 0.03125 | 0.053094 | 46 | 0.18474 | 22 | 71.6
31000 | 18245.8028 |  |  | 160 | 524.9328 | 33 | 19.423 | 0.030303 | 0.051485 | 48 | 0.19277 | 23 | 73.4
32000 | 18834.3771 |  |  |  |  | 34 | 20.0115 | 0.029412 | 0.049971 | 50 | 0.2008 | 24 | 75.2
33000 | 19422.9513 |  |  |  |  | 35 | 20.6001 | 0.028571 | 0.048543 | 52 | 0.20884 | 25 | 77
34000 | 20011.5256 |  |  |  |  | 36 | 21.1887 | 0.027778 | 0.047195 | 54 | 0.21687 | 26 | 78.8
35000 | 20600.0999 |  |  |  |  | 37 | 21.7772 | 0.027027 | 0.045919 | 56 | 0.2249 | 27 | 80.6
36000 | 21188.6742 |  |  |  |  | 38 | 22.3658 | 0.026316 | 0.044711 | 58 | 0.23293 | 28 | 82.4
37000 | 21777.2485 |  |  |  |  | 39 | 22.9544 | 0.025641 | 0.043565 | 60 | 0.24096 | 29 | 84.2
38000 | 22365.8228 |  |  |  |  | 40 | 23.543 | 0.025 | 0.042476 | 62 | 0.249 | 30 | 86
39000 | 22954.397 |  |  |  |  | 41 | 24.1315 |  |  | 64 | 0.25703 | 31 | 87.8
40000 | 23542.9713 |  |  |  |  | 42 | 24.7201 |  |  | 66 | 0.26506 | 32 | 89.6
[6 empty] | 43 | 25.3087 |  |  | 68 | 0.27309 | 33 | 91.4
50000 | 29428.7142 |  |  |  |  | 44 | 25.8973 |  |  | 70 | 0.28112 | 34 | 93.2
100000 | 58857.4283 |  |  |  |  | 45 | 26.4858 |  |  |  |  | 35 | 95
150000 | 88286.1425 |  |  |  |  | 46 | 27.0744 |  |  |  |  | 36 | 96.8
200000 | 117714.8566 |  |  |  |  | 47 | 27.663 |  |  |  |  | 37 | 98.6
250000 | 147143.5708 |  |  |  |  | 48 | 28.2516 |  |  |  |  | 38 | 100.4
300000 | 176572.2849 |  |  |  |  | 49 | 28.8401 |  |  |  |  | 39 | 102.2
350000 | 206000.9991 |  |  |  |  | 50 | 29.4287 |  |  |  |  | 40 | 104
400000 | 235429.7132 |  |  |  |  | 51 | 30.0173 |  |  |  |  | 41 | 105.8
450000 | 264858.4274 |  |  |  |  | 52 | 30.6059 |  |  |  |  | 42 | 107.6
500000 | 294287.1416 |  |  |  |  | 53 | 31.1944