## Instructions
Instructions
This spreadsheet is designed to compare the performance and costs associated with running different models of tunnel fan
It is intended to show how selecting more efficient fans can reduce energy costs over a 10 year period
| Enter values in the | Green shaded | boxes
1 | Enter shed dimensions
Then enter electricity tariff rate ($ per kW hr)
Enter 'peak power demand' rate (if applicable)*
Enter estimated number of hours per year the tunnel fans operate (the figure 2,410 hours is a calculated average from monitoring sheds in NSW, QLD and VIC)
Alternatively, enter the average number of batches per year and the typical batch length in the table below, this will estimate your minimum and maximum number of fan hours
2 | Select fans to compare
Select the fans that are currently installed on your shed (up to 5 different models)
Enter the number of fans you have installed.
The spreadsheet will then automatically calculate approximate running and other associated data
Finally, select a fan model you are considering to replace your current fans with. (up to 5 at a time can be compared, with the spreadsheet assuming only one type will be installed)
The spreadsheet will then recommend the minimum number of fans based on your shed dimensions
The speadsheet will display all associated costs. You can see how your fans compare to other models available.
Notes
* peak power demand is the network charge associated with the maximum amount of energy being drawn at any one time (usually billed as $/kW)
This spreadsheet only estimates the peak load drawn by the fans. It does not include other power consuming equipment that will effect peak load
Metric and Imperial conversion calculators are included in the 3rd and 4th worksheets
Entering custom fan data—
If a fan model you wish to compare isn't on the dropdown list, you can enter custom fan data in the second table
To gain an accurate estimation of costs, you will need to enter performance information across a range of pressures
The custom fan data will then be shown in the first comparison table, displaying associated costs
Calculator to assist with the prediction of fan hours based on fan monitoring data collected in Australia
|  |  |  | Enter maximum length of typical batch |  | 56
|  |  |  | Enter number of batches per year |  | 5.5
|  |  |  | Calculated number of production days per year |  | 308
|  |  |  | Minimum hours (on average) per fan per year |  | 1760
|  |  |  | Maximum hours (on average) per fan per year |  | 2400
Acknowledgments
This spreadsheet was developed for RIRDC project PRJ-008688, 'Reducing costs and energy by replacing inefficient ventilation fans'.
This spreadsheet was adapted from 'Tunnel-Ventilated Broiler House Fan Comparison Spreadsheet 2011', developed by The University of Georgia Biological
| and Agricultural Engineering, Michael Czarick. Available for free download at |  |  |  | http://www.poultryventilation.com/spreadsheets |  | . The spreadsheet also builds upon the
previous spreadsheet 'Review of fan efficiency in meat chicken sheds' developed for RIRDC by Mark Dunlop of the Department of Agriculture and Fisheries.
| For more information about this spreadsheet contact Grant Brown, Department of Agriculture and Fisheries |  |  |  |  | Phone (07) 4688 1521. Email grant.brown@qld.gov.au
Department of Agriculture and Fisheries
Note on I40: Use this number as the average fan hours per year. Note - the most used fans will typically do 1,500 more hours per year, than the average fans.

## Ventilation Fan Cost Calculator
Ventilation Fan Cost Calculation Spreadsheet
Refer to the INSTRUCTIONS sheet on how to use this spreadsheet.
| Enter values in | GREEN | sections (don't enter "$" or "," ). Imperial to metric conversions on the following worksheets
POULTRY HOUSE INFORMATION
House Length (m) = | 150 | Electricity Rate ($ per kW·h) = |  |  |  | 0.16
House Width (m) = | 15 | 'Peak Demand' Charge Rate ($/kW) |  |  |  | 12
Side Wall Height (m) = | 2.6 | Estimated Yearly Operating Hours per fan = |  |  |  | 2410
Ceiling Peak Height (m) = | 3 | Minimum Design Air Velocity (m/s) = |  |  |  | 3
Open/Dropped Ceiling (o/d) (m) = | o | Minimum recommended fan capacity m³/hr (air exchange) = |  |  |  | 452646.6124
Note: fan prices listed below were obtained prior to November 2013. This sheet only considers fan models with independent test report data
Select your CURRENTLY INSTALLED tunnel fan models |  |  | Number of fans | Power Consumption | Estimated Air | Total Fan | Yearly Fan | 10 Year Running Cost
|  |  | Currently installed | of Fans | Velocity in Shed | Purchase Cost | Operating Cost | Electricity | Total
|  |  |  | kW | m/s
COMBINED TOTAL
Select a possible REPLACEMENT fan from the list |  |  | Recommended | Power Consumption | Estimated Air | Total Fan | Yearly Fan | 10 Year Running Cost |  | Possible
|  |  | number of fans | of Fans | Velocity in Shed | Purchase Cost | Operating Cost | Electricity | Total | Savings
(10 year)
Custom fan data will appear here
OR ENTER CUSTOM FAN DATA BELOW
Obtain the most recent data for the fans you are considering from independent test report (available from your fan supplier).
Enter custom data |  |  | Air Flow (m³/hour) |  |  |  | Energy Efficiency | Price of Fan
(the above table will populate with estimations | [6 empty] | m³/h per watt
based on data entered here) |  |  | 12.5 Pa | 25 Pa | 37.5 Pa | 50 Pa | @ 25 Pa | ($, excl. GST)
SOURCE DATA FOR CALCULATIONS
Tunnel Fan Model |  |  | Air Flow (m³/hour) |  |  |  | Energy Efficiency | Price of Fan | Data Source
|  |  | 12.5 Pa | 25 Pa | 37.5 Pa | 50 Pa | m³/h per watt @ 25 Pa | ($, excl. GST)
Custom Fan 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0
Custom Fan 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0
Custom Fan 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0
Custom Fan 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0
Custom Fan 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0
Hired Hand 6603-7403 52" (60Hz) CONE 1hp |  |  | 46553 | 43665 | 40946 | 37548 | 35 | 1133 | BESS test 02466
Hired Hand 6603-6527 52.5" - Butterfly damper (60Hz) CONE 1hp |  |  | 46720 | 43665 | 39925 | 35850 | 32.8 | 1198.32 | BESS test 05334
Hired Hand 6603-3000 52.5" - CONE 1.5hp |  |  | 43665 | 40605 | 37038 | 32790 | 32.96 | 1542.09 | BESS test 07090
Hired Hand 6603-8010 54" - CONE 1.5hp |  |  | 45363 | 42645 | 39417 | 35509 | 41.14 | 1464 | BESS test 08257a
Munters Euroemme EM50 - 1hp |  |  | 32978 | 30786 | 27713 | 24365 | 26.5 | 908 | BESS test 02333
Munters Euroemme EM50 - 1.5hp |  |  | 40042 | 38272 | 36028 | 33717 | 21.76 | 931.25 | BESS test 02332
Munters Euroemme EC-50 (60Hz, 1 phase) CONE 1hp |  |  | 38590 | 35870 | 32640 | 28560 | 33.66 | 1101 | BESS test 02335
Munters Euroemme EC-50 CONE 1.5hp |  |  | 44401.413 | 42526.1004 | 40450.726 | 38017.6614 | 26.7323 | 1121 | BESS test 02334
Munters WF541V3CD-50 – Butterfly damper, 54" (1hp, CONE) |  |  | 44300 | 40800 | 36900 | 32600 | 36.5 | 1550 | BESS test 11353
Munters WF501V3CD-50 – Butterfly damper, 50" (1hp, CONE) |  |  | 40800 | 36800 | 30300 | 26300 | 31.9 | 1500 | BESS test 11351
Munters WF5015V3CD-50 – Butterfly damper, 50" (1.5hp, CONE) |  |  | 44600 | 41500 | 37900 | 34200 | 30.1 | 1500 | Best test 11352
American Coolair MNBF60M (60Hz) 1.5 hp |  |  | 49470 | 46070 | 41310 | 34340 | 31.2 | 2189 | BESS test 09248
American Coolair MNBFC60M (60Hz) CONE 1.5 hp |  |  | 54400 | 50320 | 44880 | 36890 | 33.8 | 2445 | BESS test 09257
American Coolair MNBFA54L (60Hz) 1hp |  |  | 40235.6 | 37655 | 34690.2 | 29998.2 | 32.64 | 1758 | American Coolair brochure Jan 2010 (ANSI/AMCA Standard 210-07)
American Coolair MNBFA54M (60Hz) 1.5hp) |  |  | 45042 | 42720 | 40294 | 37303 | 26.33 | 1830 | American Coolair brochure Jan 2010 (ANSI/AMCA Standard 210-07)
American Coolair MNBFA54N (60Hz) 2hp |  |  | 48875 | 46711 | 44529 | 42089.6 | 20.1 | 1892 | American Coolair brochure Jan 2010 (ANSI/AMCA Standard 210-07)
American Coolair MNBFA48L (60Hz) 1hp with CONE |  |  | 31387 | 29053 | 26651 | 23774 | 31.3 | 1458 | American Coolair brochure Jan 2010 (ANSI/AMCA Standard 210-07)
American Coolair MNCFC52L (60Hz) CONE 1hp |  |  | 41310 | 37570 | 33150 | 26350 | 30.43 | 1708 | American Coolair brochure Oct 2007 (ANSI/AMCA Standard 210-99)
American Coolair MNBCCE54L (60 Hz) CONE 1hp |  |  | 43494 | 40266 | 36019 | 30752 | 46.2 | 1888 | BESS test 10240
American Coolair MNCFE52L (60Hz) 1hp |  |  | 35530 | 32300 | 28050 | 21590 | 33.49 | 1470 | BESS test 99160
Chore-Time 52157-51 (54", 1.5hp, 3 blade) CONE |  |  | 51310 | 47912 | 43834 | 39926 | 33.8 | 1542 | BESS test 09084
Multifan MF130 0.75kW (50.5", 1.0hp, 3 blade) |  |  | 35400 | 32100 | 27200 | 22500 | 27.3 | 720 | BESS test 12123
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) |  |  | 40200 | 37800 | 34600 | 30600 | 25.4 | 720 | BESS test 12126
Multifan MF130 0.75 kW (50.5", 1.0 hp, 3 blade) CONE |  |  | 38800 | 35800 | 32400 | 28200 | 30.6 | 890 | BESS test 12136
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) CONE |  |  | 44100 | 41700 | 38900 | 36100 | 28.5 | 890 | BESS test 12138
Outputs per Shed—for custom number of fans | [11 empty] | EVAPORATIVE COOLING PAD REQUIREMENTS |  |  | TOTAL FAN RUNNING COSTS PER SHED
Model # |  |  | Design static | Tunnel Fan | Number of fans | Change number | Total air moving capacity | Power Consumption | Total fan operating | Air velocity | Est. Wind-chill @ 29.4°C | Total Pad Area | Pad water usage | Pad water usage |  | Five Year |  | Ten Year |  | Peak Power |  | Energy Eff. | Pressure | m³/hr for velocity | velocity check | Airflow for Evap
|  |  | pressure | capacity | required * | of fans? (no=0) | at design static pressure | All fans @ 25 Pa | cost (yearly) | (all fans operating) | (all fans operating) | (minimum for 150mm thick pad) | (32.2°C - 50% Rh) | (37.8°C - 20 % Rh) | Purchase cost | Electricity | Total | Electricity | Total | Yearly Costs | 10 Year Costs | Rating | Rating |  |  | cooling Calcs
Custom Fan 1 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Custom Fan 2 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Custom Fan 3 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Custom Fan 4 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Custom Fan 5 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Hired Hand 6603-7403 52" (60Hz) CONE 1hp |  |  | 37.5 | 40946 | 12 | 0 | 491400 | 15 | 6760 | 3.25 | 9.4164 | 81.4576 | 1641.276 | 3100.734 | 13596 | 33800 | 47396 | 67600 | 81196 | 990 | 9900 | 2 | 0 | 453600 | 453600 | 46553
Hired Hand 6603-6527 52.5" - Butterfly damper (60Hz) CONE 1hp |  |  | 37.5 | 39925 | 12 | 0 | 479100 | 16 | 7216 | 3.17 | 8.9645 | 81.7498 | 1600.194 | 3023.121 | 14379.84 | 36080 | 50459.84 | 72160 | 86539.84 | 1056 | 10560 | 1 | 0 | 453600 | 453600 | 46720
Hired Hand 6603-3000 52.5" - CONE 1.5hp |  |  | 37.5 | 37038 | 13 | 0 | 481500 | 16 | 7236 | 3.18 | 9.0204 | 82.7712 | 1608.21 | 3038.265 | 20047.17 | 36180 | 56227.17 | 72360 | 92407.17 | 1056 | 10560 | 1 | 0 | 453600 | 453600 | 43665
Hired Hand 6603-8010 54" - CONE 1.5hp |  |  | 37.5 | 39417 | 12 | 0 | 473000 | 12.4 | 5618.4 | 3.13 | 8.7427 | 79.3753 | 1579.82 | 2984.63 | 17568 | 28092 | 45660 | 56184 | 73752 | 818.4 | 8184 | 4 | 0 | 453600 | 453600 | 45363
Munters Euroemme EM50 - 1hp |  |  | 37.5 | 27713 | 17 | 0 | 471100 | 19.7 | 8920.2 | 3.12 | 8.6877 | 81.7477 | 1573.474 | 2972.641 | 15436 | 44601 | 60037 | 89202 | 104638 | 1300.2 | 13002 | 0 | 0 | 453600 | 453600 | 32978
Munters Euroemme EM50 - 1.5hp |  |  | 37.5 | 36028 | 13 | 0 | 468400 | 22.9 | 10331.4 | 3.1 | 8.5782 | 75.9035 | 1564.456 | 2955.604 | 12106.25 | 51657 | 63763.25 | 103314 | 115420.25 | 1511.4 | 15114 | 0 | 0 | 453600 | 453600 | 40042
Munters Euroemme EC-50 (60Hz, 1 phase) CONE 1hp |  |  | 37.5 | 32640 | 14 | 0 | 457000 | 14.9 | 6733.4 | 3.02 | 8.1471 | 78.7781 | 1526.38 | 2883.67 | 15414 | 33667 | 49081 | 67334 | 82748 | 983.4 | 9834 | 1 | 0 | 453600 | 453600 | 38590
Munters Euroemme EC-50 CONE 1.5hp |  |  | 37.5 | 40450.726 | 12 | 0 | 485400 | 19.1 | 8620.6 | 3.21 | 9.1891 | 77.6928 | 1621.236 | 3062.874 | 13452 | 43103 | 56555 | 86206 | 99658 | 1260.6 | 12606 | 0 | 0 | 453600 | 453600 | 44401.413
Munters WF541V3CD-50 – Butterfly damper, 54" (1hp, CONE) |  |  | 37.5 | 36900 | 13 | 0 | 479700 | 14.5 | 6557 | 3.17 | 8.9645 | 83.9749 | 1602.198 | 3026.907 | 20150 | 32785 | 52935 | 65570 | 85720 | 957 | 9570 | 3 | 0 | 453600 | 453600 | 44300
Munters WF501V3CD-50 – Butterfly damper, 50" (1hp, CONE) |  |  | 37.5 | 30300 | 15 | 0 | 454500 | 17.3 | 7811.8 | 3.01 | 8.094 | 89.2388 | 1518.03 | 2867.895 | 22500 | 39059 | 61559 | 78118 | 100618 | 1141.8 | 11418 | 0 | 0 | 453600 | 453600 | 40800
Munters WF5015V3CD-50 – Butterfly damper, 50" (1.5hp, CONE) |  |  | 37.5 | 37900 | 12 | 0 | 454800 | 16.5 | 7469 | 3.01 | 8.094 | 78.0402 | 1519.032 | 2869.788 | 18000 | 37345 | 55345 | 74690 | 92690 | 1089 | 10890 | 0 | 0 | 453600 | 453600 | 44600
American Coolair MNBF60M (60Hz) 1.5 hp |  |  | 37.5 | 41310 | 11 | 0 | 454400 | 16.2 | 7329.2 | 3.01 | 8.094 | 79.3482 | 1517.696 | 2867.264 | 24079 | 36646 | 60725 | 73292 | 97371 | 1069.2 | 10692 | 0 | 0 | 453600 | 453600 | 49470
American Coolair MNBFC60M (60Hz) CONE 1.5 hp |  |  | 37.5 | 44880 | 11 | 0 | 493700 | 16.4 | 7392.4 | 3.27 | 9.5311 | 87.2558 | 1648.958 | 3115.247 | 26895 | 36962 | 63857 | 73924 | 100819 | 1082.4 | 10824 | 1 | 0 | 453600 | 453600 | 54400
American Coolair MNBFA54L (60Hz) 1hp |  |  | 37.5 | 34690.2 | 14 | 0 | 485700 | 16.2 | 7299.2 | 3.21 | 9.1891 | 82.1374 | 1622.238 | 3064.767 | 24612 | 36496 | 61108 | 72992 | 97604 | 1069.2 | 10692 | 1 | 0 | 453600 | 453600 | 40235.6
American Coolair MNBFA54M (60Hz) 1.5hp) |  |  | 37.5 | 40294 | 12 | 0 | 483500 | 19.5 | 8797 | 3.2 | 9.1327 | 78.8136 | 1614.89 | 3050.885 | 21960 | 43985 | 65945 | 87970 | 109930 | 1287 | 12870 | 0 | 0 | 453600 | 453600 | 45042
American Coolair MNBFA54N (60Hz) 2hp |  |  | 37.5 | 44529 | 11 | 0 | 489800 | 25.6 | 11549.6 | 3.24 | 9.3593 | 78.3938 | 1635.932 | 3090.638 | 20812 | 57748 | 78560 | 115496 | 136308 | 1689.6 | 16896 | 0 | 0 | 453600 | 453600 | 48875
American Coolair MNBFA48L (60Hz) 1hp with CONE |  |  | 37.5 | 26651 | 18 | 0 | 479700 | 16.7 | 7542.2 | 3.17 | 8.9645 | 82.3806 | 1602.198 | 3026.907 | 26244 | 37711 | 63955 | 75422 | 101666 | 1102.2 | 11022 | 0 | 0 | 453600 | 453600 | 31387
American Coolair MNCFC52L (60Hz) CONE 1hp |  |  | 37.5 | 33150 | 14 | 0 | 464100 | 17.3 | 7811.8 | 3.07 | 8.4153 | 84.3307 | 1550.094 | 2928.471 | 23912 | 39059 | 62971 | 78118 | 102030 | 1141.8 | 11418 | 0 | 0 | 453600 | 453600 | 41310
American Coolair MNBCCE54L (60 Hz) CONE 1hp |  |  | 37.5 | 36019 | 13 | 0 | 468200 | 11.3 | 5115.8 | 3.1 | 8.5782 | 82.4471 | 1563.788 | 2954.342 | 24544 | 25579 | 50123 | 51158 | 75702 | 745.8 | 7458 | 4 | 0 | 453600 | 453600 | 43494
American Coolair MNCFE52L (60Hz) 1hp |  |  | 37.5 | 28050 | 17 | 0 | 476900 | 16.4 | 7402.4 | 3.15 | 8.8533 | 88.0738 | 1592.846 | 3009.239 | 24990 | 37012 | 62002 | 74024 | 99014 | 1082.4 | 10824 | 1 | 0 | 453600 | 453600 | 35530
Chore-Time 52157-51 (54", 1.5hp, 3 blade) CONE |  |  | 37.5 | 43834 | 11 | 0 | 482200 | 15.6 | 7039.6 | 3.19 | 9.0764 | 82.2995 | 1610.548 | 3042.682 | 16962 | 35198 | 52160 | 70396 | 87358 | 1029.6 | 10296 | 1 | 0 | 453600 | 453600 | 51310
Multifan MF130 0.75kW (50.5", 1.0hp, 3 blade) |  |  | 37.5 | 27200 | 17 | 0 | 462400 | 20 | 9030 | 3.06 | 8.3613 | 87.7515 | 1544.416 | 2917.744 | 12240 | 45150 | 57390 | 90300 | 102540 | 1320 | 13200 | 0 | 0 | 453600 | 453600 | 35400
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) |  |  | 37.5 | 34600 | 14 | 0 | 484400 | 20.8 | 9402.8 | 3.2 | 9.1327 | 82.0647 | 1617.896 | 3056.564 | 10080 | 47014 | 57094 | 94028 | 104108 | 1372.8 | 13728 | 0 | 0 | 453600 | 453600 | 40200
Multifan MF130 0.75 kW (50.5", 1.0 hp, 3 blade) CONE |  |  | 37.5 | 32400 | 14 | 0 | 453600 | 16.4 | 7402.4 | 3 | 8.0411 | 79.2068 | 1515.024 | 2862.216 | 12460 | 37012 | 49472 | 74024 | 86484 | 1082.4 | 10824 | 0 | 0 | 453600 | 453600 | 38800
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) CONE |  |  | 37.5 | 38900 | 12 | 0 | 466800 | 17.6 | 7931.6 | 3.09 | 8.5237 | 77.1654 | 1559.112 | 2945.508 | 10680 | 39658 | 50338 | 79316 | 89996 | 1161.6 | 11616 | 0 | 0 | 453600 | 453600 | 44100
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
Outputs per shed— for Recommended number of fans |  |  | Design static | Tunnel Fan | Number of fans | Change number | Total air moving capacity | Power Consumption | Total fan operating | Air velocity | Est. Wind-chill @ 29.4°C | Total Pad Area | Pad water usage | Pad water usage |  | Five Year |  | Ten Year |  | Peak Power |  | Energy Eff. | Pressure | m³/hr for velocity | velocity check | Airflow for Evap
|  |  | pressure | capacity | required * | of fans? (no=0) | at design static pressure | All fans @ 25 Pa | cost (yearly) | (all fans operating) | (all fans operating) | (minimum for 150mm thick pad) | (32.2°C - 50% Rh) | (37.8°C - 20 % Rh) | Purchase cost | Electricity | Total | Electricity | Total | Yearly Costs | 10 Year Costs | Rating | Rating |  |  | cooling Calcs
Custom Fan 1 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Custom Fan 2 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Custom Fan 3 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Custom Fan 4 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Custom Fan 5 |  |  | 37.5 | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 453600 | 453600 | 0
Hired Hand 6603-7403 52" (60Hz) CONE 1hp |  |  | 37.5 | 40946 | 12 | 0 | 491400 | 15 | 6760 | 3.25 | 9.4164 | 81.4576 | 1641.276 | 3100.734 | 13596 | 33800 | 47396 | 67600 | 81196 | 990 | 9900 | 2 | 0 | 453600 | 453600 | 46553
Hired Hand 6603-6527 52.5" - Butterfly damper (60Hz) CONE 1hp |  |  | 37.5 | 39925 | 12 | 0 | 479100 | 16 | 7216 | 3.17 | 8.9645 | 81.7498 | 1600.194 | 3023.121 | 14379.84 | 36080 | 50459.84 | 72160 | 86539.84 | 1056 | 10560 | 1 | 0 | 453600 | 453600 | 46720
Hired Hand 6603-3000 52.5" - CONE 1.5hp |  |  | 37.5 | 37038 | 13 | 0 | 481500 | 16 | 7236 | 3.18 | 9.0204 | 82.7712 | 1608.21 | 3038.265 | 20047.17 | 36180 | 56227.17 | 72360 | 92407.17 | 1056 | 10560 | 1 | 0 | 453600 | 453600 | 43665
Hired Hand 6603-8010 54" - CONE 1.5hp |  |  | 37.5 | 39417 | 12 | 0 | 473000 | 12.4 | 5618.4 | 3.13 | 8.7427 | 79.3753 | 1579.82 | 2984.63 | 17568 | 28092 | 45660 | 56184 | 73752 | 818.4 | 8184 | 4 | 0 | 453600 | 453600 | 45363
Munters Euroemme EM50 - 1hp |  |  | 37.5 | 27713 | 17 | 0 | 471100 | 19.7 | 8920.2 | 3.12 | 8.6877 | 81.7477 | 1573.474 | 2972.641 | 15436 | 44601 | 60037 | 89202 | 104638 | 1300.2 | 13002 | 0 | 0 | 453600 | 453600 | 32978
Munters Euroemme EM50 - 1.5hp |  |  | 37.5 | 36028 | 13 | 0 | 468400 | 22.9 | 10331.4 | 3.1 | 8.5782 | 75.9035 | 1564.456 | 2955.604 | 12106.25 | 51657 | 63763.25 | 103314 | 115420.25 | 1511.4 | 15114 | 0 | 0 | 453600 | 453600 | 40042
Munters Euroemme EC-50 (60Hz, 1 phase) CONE 1hp |  |  | 37.5 | 32640 | 14 | 0 | 457000 | 14.9 | 6733.4 | 3.02 | 8.1471 | 78.7781 | 1526.38 | 2883.67 | 15414 | 33667 | 49081 | 67334 | 82748 | 983.4 | 9834 | 1 | 0 | 453600 | 453600 | 38590
Munters Euroemme EC-50 CONE 1.5hp |  |  | 37.5 | 40450.726 | 12 | 0 | 485400 | 19.1 | 8620.6 | 3.21 | 9.1891 | 77.6928 | 1621.236 | 3062.874 | 13452 | 43103 | 56555 | 86206 | 99658 | 1260.6 | 12606 | 0 | 0 | 453600 | 453600 | 44401.413
Munters WF541V3CD-50 – Butterfly damper, 54" (1hp, CONE) |  |  | 37.5 | 36900 | 13 | 0 | 479700 | 14.5 | 6557 | 3.17 | 8.9645 | 83.9749 | 1602.198 | 3026.907 | 20150 | 32785 | 52935 | 65570 | 85720 | 957 | 9570 | 3 | 0 | 453600 | 453600 | 44300
Munters WF501V3CD-50 – Butterfly damper, 50" (1hp, CONE) |  |  | 37.5 | 30300 | 15 | 0 | 454500 | 17.3 | 7811.8 | 3.01 | 8.094 | 89.2388 | 1518.03 | 2867.895 | 22500 | 39059 | 61559 | 78118 | 100618 | 1141.8 | 11418 | 0 | 0 | 453600 | 453600 | 40800
Munters WF5015V3CD-50 – Butterfly damper, 50" (1.5hp, CONE) |  |  | 37.5 | 37900 | 12 | 0 | 454800 | 16.5 | 7469 | 3.01 | 8.094 | 78.0402 | 1519.032 | 2869.788 | 18000 | 37345 | 55345 | 74690 | 92690 | 1089 | 10890 | 0 | 0 | 453600 | 453600 | 44600
American Coolair MNBF60M (60Hz) 1.5 hp |  |  | 37.5 | 41310 | 11 | 0 | 454400 | 16.2 | 7329.2 | 3.01 | 8.094 | 79.3482 | 1517.696 | 2867.264 | 24079 | 36646 | 60725 | 73292 | 97371 | 1069.2 | 10692 | 0 | 0 | 453600 | 453600 | 49470
American Coolair MNBFC60M (60Hz) CONE 1.5 hp |  |  | 37.5 | 44880 | 11 | 0 | 493700 | 16.4 | 7392.4 | 3.27 | 9.5311 | 87.2558 | 1648.958 | 3115.247 | 26895 | 36962 | 63857 | 73924 | 100819 | 1082.4 | 10824 | 1 | 0 | 453600 | 453600 | 54400
American Coolair MNBFA54L (60Hz) 1hp |  |  | 37.5 | 34690.2 | 14 | 0 | 485700 | 16.2 | 7299.2 | 3.21 | 9.1891 | 82.1374 | 1622.238 | 3064.767 | 24612 | 36496 | 61108 | 72992 | 97604 | 1069.2 | 10692 | 1 | 0 | 453600 | 453600 | 40235.6
American Coolair MNBFA54M (60Hz) 1.5hp) |  |  | 37.5 | 40294 | 12 | 0 | 483500 | 19.5 | 8797 | 3.2 | 9.1327 | 78.8136 | 1614.89 | 3050.885 | 21960 | 43985 | 65945 | 87970 | 109930 | 1287 | 12870 | 0 | 0 | 453600 | 453600 | 45042
American Coolair MNBFA54N (60Hz) 2hp |  |  | 37.5 | 44529 | 11 | 0 | 489800 | 25.6 | 11549.6 | 3.24 | 9.3593 | 78.3938 | 1635.932 | 3090.638 | 20812 | 57748 | 78560 | 115496 | 136308 | 1689.6 | 16896 | 0 | 0 | 453600 | 453600 | 48875
American Coolair MNBFA48L (60Hz) 1hp with CONE |  |  | 37.5 | 26651 | 18 | 0 | 479700 | 16.7 | 7542.2 | 3.17 | 8.9645 | 82.3806 | 1602.198 | 3026.907 | 26244 | 37711 | 63955 | 75422 | 101666 | 1102.2 | 11022 | 0 | 0 | 453600 | 453600 | 31387
American Coolair MNCFC52L (60Hz) CONE 1hp |  |  | 37.5 | 33150 | 14 | 0 | 464100 | 17.3 | 7811.8 | 3.07 | 8.4153 | 84.3307 | 1550.094 | 2928.471 | 23912 | 39059 | 62971 | 78118 | 102030 | 1141.8 | 11418 | 0 | 0 | 453600 | 453600 | 41310
American Coolair MNBCCE54L (60 Hz) CONE 1hp |  |  | 37.5 | 36019 | 13 | 0 | 468200 | 11.3 | 5115.8 | 3.1 | 8.5782 | 82.4471 | 1563.788 | 2954.342 | 24544 | 25579 | 50123 | 51158 | 75702 | 745.8 | 7458 | 4 | 0 | 453600 | 453600 | 43494
American Coolair MNCFE52L (60Hz) 1hp |  |  | 37.5 | 28050 | 17 | 0 | 476900 | 16.4 | 7402.4 | 3.15 | 8.8533 | 88.0738 | 1592.846 | 3009.239 | 24990 | 37012 | 62002 | 74024 | 99014 | 1082.4 | 10824 | 1 | 0 | 453600 | 453600 | 35530
Chore-Time 52157-51 (54", 1.5hp, 3 blade) CONE |  |  | 37.5 | 43834 | 11 | 0 | 482200 | 15.6 | 7039.6 | 3.19 | 9.0764 | 82.2995 | 1610.548 | 3042.682 | 16962 | 35198 | 52160 | 70396 | 87358 | 1029.6 | 10296 | 1 | 0 | 453600 | 453600 | 51310
Multifan MF130 0.75kW (50.5", 1.0hp, 3 blade) |  |  | 37.5 | 27200 | 17 | 0 | 462400 | 20 | 9030 | 3.06 | 8.3613 | 87.7515 | 1544.416 | 2917.744 | 12240 | 45150 | 57390 | 90300 | 102540 | 1320 | 13200 | 0 | #REF! | 453600 | 453600 | 35400
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) |  |  | 37.5 | 34600 | 14 | 0 | 484400 | 20.8 | 9402.8 | 3.2 | 9.1327 | 82.0647 | 1617.896 | 3056.564 | 10080 | 47014 | 57094 | 94028 | 104108 | 1372.8 | 13728 | 0 | #REF! | 453600 | 453600 | 40200
Multifan MF130 0.75 kW (50.5", 1.0 hp, 3 blade) CONE |  |  | 37.5 | 32400 | 14 | 0 | 453600 | 16.4 | 7402.4 | 3 | 8.0411 | 79.2068 | 1515.024 | 2862.216 | 12460 | 37012 | 49472 | 74024 | 86484 | 1082.4 | 10824 | 0 | 0 | 453600 | 453600 | 38800
Multifan MF130 1.12 kW (50.5", 1.5 hp, 3 blade) CONE |  |  | 37.5 | 38900 | 12 | 0 | 466800 | 17.6 | 7931.6 | 3.09 | 8.5237 | 77.1654 | 1559.112 | 2945.508 | 10680 | 39658 | 50338 | 79316 | 89996 | 1161.6 | 11616 | 0 | 0 | 453600 | 453600 | 44100
[5 empty] | #VALUE! |  |  |  | #VALUE! | [6 empty] | #VALUE! |  | #VALUE! |  | #VALUE! | #VALUE! |  | 0 | 453600 | 453600 | 0
[5 empty] | #VALUE! |  |  |  | #VALUE! | [6 empty] | #VALUE! |  | #VALUE! |  | #VALUE! | #VALUE! |  | 0 | 453600 | 453600 | 0
[20 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
[6 empty] | 0 | [13 empty] | #VALUE! | #VALUE! |  |  | 453600 | 453600 | 0
Note on H6: Note: Some farms may be billed for kVa rather than kW.
Note on H7: Note: Peak power demand is the network charge associated with the maximum amount of energy being drawn at any one time. If unsure if you are billed this way, leave as '0.00'.
Note on H8: Note: Use the table in INSTRUCTIONS sheet to assist with estimating the number of yearly fan operating hours. 2,410 hours is a calculated average based on monitoring broiler sheds in NSW, QLD and VIC.
Note on C9: Note: if you have ceiling baffles, set the 'Ceiling Peak Height' to the height of the baffle above the shed floor.
Note on C10: Note: Dropped ceilings are used in the United States but rarely seen in Australia. If unsure, leave as is.
Note on G25: Note: Shed air velocity should be greater than 3.00m/s
Note on E107: This is the pressure at the fans, so will usually be greater than the shed static pressure
Note on J107: Note: if calculating peak power load, you may need to use the power consumption at higher static pressure - refer to your fan test report
Note on R108: Based on Poultry Housing Tips—Pad System Cooling, Installation and Management. (July 2001, vol. 13 No.8 — 1m² per 6858 m³/hr
Note on S108: Based on Poultry Housing Tips—Six-inch pad system water usage and pipe sizing. (June 2006, vol. 18 No.6
Note on Z108: Based on hitting peak load once per batch
Note on E151: This is the pressure at the fans, so will usually be greater than the shed static pressure
Note on J151: Note: if calculating peak power load, you may need to use the power consumption at higher static pressure - refer to your fan test report
Note on R152: Based on Poultry Housing Tips—Pad System Cooling, Installation and Management. (July 2001, vol. 13 No.8 — 1m² per 6858 m³/hr
Note on S152: Based on Poultry Housing Tips—Six-inch pad system water usage and pipe sizing. (June 2006, vol. 18 No.6
Note on Z152: Based on hitting peak load once per batch

## Imperial to metric Conv.
To convert Imperial/English units into metric, type the Imperial/English value into the green cell and press ENTER. Read the metric value from the cell with green text
Flow rate |  |  | Speed |  | Distance |  | Energy Efficiency |  | Pressure |  | Temperature
CFM | m³/h | m³/s | feet/min | m/s | ft | m | CFM per watt | m³/h per watt | inch H2O | Pa | °F | °C
1 | 2 | 0.001 | 1 | 0.01 | 1 | 0.3048 | 1 | 1.699 | 0.2 | 49.8 | 1 | -17.2222
2000 | 3398.0418 | 0.9439 | 50 | 0.254 | 10 | 3.048 | 10 | 16.9902 | 0.01 | 2.49 | 32 | 0
2500 | 4247.5522 | 1.1799 | 100 | 0.508 | 15 | 4.572 | 11 | 18.6892 | 0.02 | 4.98 | 34 | 1.1111
3000 | 5097.0627 | 1.4159 | 150 | 0.762 | 20 | 6.096 | 12 | 20.3883 | 0.03 | 7.47 | 36 | 2.2222
3500 | 5946.5731 | 1.6518 | 200 | 1.016 | 25 | 7.62 | 13 | 22.0873 | 0.04 | 9.96 | 38 | 3.3333
4000 | 6796.0835 | 1.8878 | 250 | 1.27 | 30 | 9.144 | 14 | 23.7863 | 0.05 | 12.45 | 40 | 4.4444
4500 | 7645.594 | 2.1238 | 300 | 1.524 | 35 | 10.668 | 15 | 25.4853 | 0.06 | 14.94 | 42 | 5.5556
5000 | 8495.1044 | 2.3598 | 350 | 1.778 | 40 | 12.192 | 16 | 27.1843 | 0.07 | 17.43 | 44 | 6.6667
5500 | 9344.6149 | 2.5957 | 400 | 2.032 | 45 | 13.716 | 17 | 28.8834 | 0.08 | 19.92 | 46 | 7.7778
6000 | 10194.1253 | 2.8317 | 450 | 2.286 | 50 | 15.24 | 18 | 30.5824 | 0.09 | 22.41 | 48 | 8.8889
6500 | 11043.6358 | 3.0677 | 500 | 2.54 | 55 | 16.764 | 19 | 32.2814 | 0.1 | 24.9 | 50 | 10
7000 | 11893.1462 | 3.3037 | 550 | 2.794 | 60 | 18.288 | 20 | 33.9804 | 0.11 | 27.39 | 52 | 11.1111
7500 | 12742.6566 | 3.5396 | 600 | 3.048 | 65 | 19.812 | 21 | 35.6794 | 0.12 | 29.88 | 54 | 12.2222
8000 | 13592.1671 | 3.7756 | 650 | 3.302 | 100 | 30.4801 | 22 | 37.3785 | 0.13 | 32.37 | 56 | 13.3333
8500 | 14441.6775 | 4.0116 | 700 | 3.556 | 300 | 91.4402 | 23 | 39.0775 | 0.14 | 34.86 | 58 | 14.4444
9000 | 15291.188 | 4.2476 | 750 | 3.81 | 350 | 106.6802 | 24 | 40.7765 | 0.15 | 37.35 | 60 | 15.5556
9500 | 16140.6984 | 4.4835 | 800 | 4.064 | 400 | 121.9202 | 25 | 42.4755 | 0.16 | 39.84 | 62 | 16.6667
10000 | 16990.2089 | 4.7195 | 850 | 4.318 | 450 | 137.1603 | 26 | 44.1745 | 0.17 | 42.33 | 64 | 17.7778
10500 | 17839.7193 | 4.9555 | 900 | 4.572 | 500 | 152.4003 | 27 | 45.8736 | 0.18 | 44.82 | 66 | 18.8889
11000 | 18689.2297 | 5.1915 |  |  | 550 | 167.6403 | 28 | 47.5726 | 0.19 | 47.31 | 68 | 20
11500 | 19538.7402 | 5.4274 |  |  | 600 | 182.8804 | 29 | 49.2716 | 0.2 | 49.8 | 70 | 21.1111
12000 | 20388.2506 | 5.6634 |  |  | 650 | 198.1204 | 30 | 50.9706 | 0.21 | 52.29 | 72 | 22.2222
12500 | 21237.7611 | 5.8994 |  |  | 700 | 213.3604 |  |  | 0.22 | 54.78 | 74 | 23.3333
13000 | 22087.2715 | 6.1354 |  |  | 750 | 228.6005 | Energy Efficiency |  | 0.23 | 57.27 | 76 | 24.4444
13500 | 22936.782 | 6.3713 |  |  |  |  | Watts per CFM | Watts per m³/h | 0.24 | 59.76 | 78 | 25.5556
14000 | 23786.2924 | 6.6073 |  |  |  |  | 1 | 0.58857 | 0.25 | 62.25 | 80 | 26.6667
14500 | 24635.8028 | 6.8433 |  |  |  |  | 0.1 | 0.058857 | 0.26 | 64.74 | 82 | 27.7778
15000 | 25485.3133 | 7.0793 |  |  |  |  | 0.090909 | 0.053507 | 0.27 | 67.23 | 84 | 28.8889
15500 | 26334.8237 | 7.3152 |  |  |  |  | 0.083333 | 0.049048 | 0.28 | 69.72 | 86 | 30
16000 | 27184.3342 | 7.5512 |  |  |  |  | 0.076923 | 0.045275 | 0.29 | 72.21 | 88 | 31.1111
16500 | 28033.8446 | 7.7872 |  |  |  |  | 0.071429 | 0.042041 | 0.3 | 74.7 | 90 | 32.2222
17000 | 28883.3551 | 8.0232 |  |  |  |  | 0.066667 | 0.039238 |  |  | 92 | 33.3333
17500 | 29732.8655 | 8.2591 |  |  |  |  | 0.0625 | 0.036786 |  |  | 94 | 34.4444
18000 | 30582.3759 | 8.4951 |  |  |  |  | 0.058824 | 0.034622 |  |  | 96 | 35.5556
18500 | 31431.8864 | 8.7311 |  |  |  |  | 0.055556 | 0.032699 |  |  | 98 | 36.6667
19000 | 32281.3968 | 8.9671 |  |  |  |  | 0.052632 | 0.030978 |  |  | 100 | 37.7778
19500 | 33130.9073 | 9.203 |  |  |  |  | 0.05 | 0.029429 |  |  | 102 | 38.8889
20000 | 33980.4177 | 9.439 |  |  |  |  | 0.047619 | 0.028027 |  |  | 104 | 40
20500 | 34829.9282 | 9.675 |  |  |  |  | 0.045455 | 0.026753 |  |  | 106 | 41.1111
21000 | 35679.4386 | 9.911 |  |  |  |  | 0.043478 | 0.02559 |  |  | 108 | 42.2222
[7 empty] | 0.041667 | 0.024524
50000 | 84951.0443 | 23.5975 |  |  |  |  | 0.04 | 0.023543
100000 | 169902.0886 | 47.195 |  |  |  |  | 0.038462 | 0.022637
150000 | 254853.1329 | 70.7925 |  |  |  |  | 0.037037 | 0.021799
200000 | 339804.1772 | 94.39 |  |  |  |  | 0.035714 | 0.021021
250000 | 424755.2215 | 117.9876 |  |  |  |  | 0.034483 | 0.020296
300000 | 509706.2658 | 141.5851 |  |  |  |  | 0.033333 | 0.019619

## Metric to Imperial Conv.
To convert metric units into Imperial/English, type the metric value into the green cell and press ENTER. Read the Imperial/English value from the cell with green text
Flow Rate |  | Speed |  | Distance |  | Energy Efficiency |  | Energy Efficiency |  | Pressure |  | Temperature
m³/h | CFM | m/s | feet/min | m | ft | m³/h per watt | CFM per watt | Watts per m³/h | Watts per CFM | Pa | inch H2O | °C | °F
1 | 0.58857 | 1 | 196.85 | 1 | 3.2808 | 1 | 0.58857 | 1 | 1.699 | 1 | 0.0040161 | 1 | 33.8
1000 | 588.5743 | 0.25 | 49.2125 | 5 | 16.4042 | 10 | 5.8857 | 0.1 | 0.1699 | 2 | 0.0080321 | 0 | 32
5000 | 2942.8714 | 0.5 | 98.425 | 6 | 19.685 | 11 | 6.4743 | 0.090909 | 0.15446 | 4 | 0.016064 | 1 | 33.8
10000 | 5885.7428 | 0.75 | 147.6375 | 7 | 22.9658 | 12 | 7.0629 | 0.083333 | 0.14159 | 6 | 0.024096 | 2 | 35.6
11000 | 6474.3171 | 1 | 196.85 | 8 | 26.2466 | 13 | 7.6515 | 0.076923 | 0.13069 | 8 | 0.032129 | 3 | 37.4
12000 | 7062.8914 | 1.25 | 246.0625 | 9 | 29.5275 | 14 | 8.24 | 0.071429 | 0.12136 | 10 | 0.040161 | 4 | 39.2
13000 | 7651.4657 | 1.5 | 295.275 | 10 | 32.8083 | 15 | 8.8286 | 0.066667 | 0.11327 | 12 | 0.048193 | 5 | 41
14000 | 8240.04 | 1.75 | 344.4875 | 11 | 36.0891 | 16 | 9.4172 | 0.0625 | 0.10619 | 14 | 0.056225 | 6 | 42.8
15000 | 8828.6142 | 2 | 393.7 | 12 | 39.37 | 17 | 10.0058 | 0.058824 | 0.099942 | 16 | 0.064257 | 7 | 44.6
16000 | 9417.1885 | 2.25 | 442.9125 | 13 | 42.6508 | 18 | 10.5943 | 0.055556 | 0.09439 | 18 | 0.072289 | 8 | 46.4
17000 | 10005.7628 | 2.5 | 492.125 | 14 | 45.9316 | 19 | 11.1829 | 0.052632 | 0.089422 | 20 | 0.080321 | 9 | 48.2
18000 | 10594.3371 | 2.75 | 541.3375 | 15 | 49.2124 | 20 | 11.7715 | 0.05 | 0.084951 | 22 | 0.088353 | 10 | 50
19000 | 11182.9114 | 3 | 590.55 | 16 | 52.4933 | 21 | 12.3601 | 0.047619 | 0.080906 | 24 | 0.096386 | 11 | 51.8
20000 | 11771.4857 | 3.25 | 639.7625 | 17 | 55.7741 | 22 | 12.9486 | 0.045455 | 0.077228 | 26 | 0.10442 | 12 | 53.6
21000 | 12360.0599 | 3.5 | 688.975 | 18 | 59.0549 | 23 | 13.5372 | 0.043478 | 0.07387 | 28 | 0.11245 | 13 | 55.4
22000 | 12948.6342 | 3.75 | 738.1875 | 19 | 62.3358 | 24 | 14.1258 | 0.041667 | 0.070793 | 30 | 0.12048 | 14 | 57.2
23000 | 13537.2085 | 4 | 787.4 | 20 | 65.6166 | 25 | 14.7144 | 0.04 | 0.067961 | 32 | 0.12851 | 15 | 59
24000 | 14125.7828 | 4.25 | 836.6125 |  |  | 26 | 15.3029 | 0.038462 | 0.065347 | 34 | 0.13655 | 16 | 60.8
25000 | 14714.3571 | 4.5 | 885.825 | 100 | 328.083 | 27 | 15.8915 | 0.037037 | 0.062927 | 36 | 0.14458 | 17 | 62.6
26000 | 15302.9314 | 4.75 | 935.0375 | 110 | 360.8913 | 28 | 16.4801 | 0.035714 | 0.060679 | 38 | 0.15261 | 18 | 64.4
27000 | 15891.5056 |  |  | 120 | 393.6996 | 29 | 17.0687 | 0.034483 | 0.058587 | 40 | 0.16064 | 19 | 66.2
28000 | 16480.0799 |  |  | 130 | 426.5079 | 30 | 17.6572 | 0.033333 | 0.056634 | 42 | 0.16867 | 20 | 68
29000 | 17068.6542 |  |  | 140 | 459.3162 | 31 | 18.2458 | 0.032258 | 0.054807 | 44 | 0.17671 | 21 | 69.8
30000 | 17657.2285 |  |  | 150 | 492.1245 | 32 | 18.8344 | 0.03125 | 0.053094 | 46 | 0.18474 | 22 | 71.6
31000 | 18245.8028 |  |  | 160 | 524.9328 | 33 | 19.423 | 0.030303 | 0.051485 | 48 | 0.19277 | 23 | 73.4
32000 | 18834.3771 |  |  |  |  | 34 | 20.0115 | 0.029412 | 0.049971 | 50 | 0.2008 | 24 | 75.2
33000 | 19422.9513 |  |  |  |  | 35 | 20.6001 | 0.028571 | 0.048543 | 52 | 0.20884 | 25 | 77
34000 | 20011.5256 |  |  |  |  | 36 | 21.1887 | 0.027778 | 0.047195 | 54 | 0.21687 | 26 | 78.8
35000 | 20600.0999 |  |  |  |  | 37 | 21.7772 | 0.027027 | 0.045919 | 56 | 0.2249 | 27 | 80.6
36000 | 21188.6742 |  |  |  |  | 38 | 22.3658 | 0.026316 | 0.044711 | 58 | 0.23293 | 28 | 82.4
37000 | 21777.2485 |  |  |  |  | 39 | 22.9544 | 0.025641 | 0.043565 | 60 | 0.24096 | 29 | 84.2
38000 | 22365.8228 |  |  |  |  | 40 | 23.543 | 0.025 | 0.042476 | 62 | 0.249 | 30 | 86
39000 | 22954.397 |  |  |  |  | 41 | 24.1315 |  |  | 64 | 0.25703 | 31 | 87.8
40000 | 23542.9713 |  |  |  |  | 42 | 24.7201 |  |  | 66 | 0.26506 | 32 | 89.6
[6 empty] | 43 | 25.3087 |  |  | 68 | 0.27309 | 33 | 91.4
50000 | 29428.7142 |  |  |  |  | 44 | 25.8973 |  |  | 70 | 0.28112 | 34 | 93.2
100000 | 58857.4283 |  |  |  |  | 45 | 26.4858 |  |  |  |  | 35 | 95
150000 | 88286.1425 |  |  |  |  | 46 | 27.0744 |  |  |  |  | 36 | 96.8
200000 | 117714.8566 |  |  |  |  | 47 | 27.663 |  |  |  |  | 37 | 98.6
250000 | 147143.5708 |  |  |  |  | 48 | 28.2516 |  |  |  |  | 38 | 100.4
300000 | 176572.2849 |  |  |  |  | 49 | 28.8401 |  |  |  |  | 39 | 102.2
350000 | 206000.9991 |  |  |  |  | 50 | 29.4287 |  |  |  |  | 40 | 104
400000 | 235429.7132 |  |  |  |  | 51 | 30.0173 |  |  |  |  | 41 | 105.8
450000 | 264858.4274 |  |  |  |  | 52 | 30.6059 |  |  |  |  | 42 | 107.6
500000 | 294287.1416 |  |  |  |  | 53 | 31.1944